Applied Thermal Engineering 182 (2021) 116013

Contents lists available at ScienceDirect

Applied Thermal Engineering

journal homepage: www.elsevier.com/locate/apthermeng

Performance assessment of a shell and helically coiled tube heat exchanger	 with variable orientations utilizing different nanofluids

Hussein M. Maghrabie *, M. Attalla, Abrar A. A. Mohsen

Department of Mechanical Engineering, Faculty of Engineering, South Valley University, Qena 83521, Egypt

A R T I C L E I N F O

Keywords:

SHCT-HE

Nanofluids Inclination angle Coil Nusselt number

Performance evaluation criterion Multiple regression analysis

A B S T R A C T

In the present study, the effect of the inclination angle (ɵ) of a shell and helically coiled tube heat exchanger (SHCT-HE) on its performance utilizing based water, Al2O3/water, and SiO2/water nanofluids is investigated experimentally. The hot based water as well as nanofluids with volume concentrations (ϕ) of 0.1 vol%, 0.2 vol%, and 0.3 vol% flow through the coiled tube with a coil Reynolds number (Rec) varied from 6000 to 15000. The inclination angle is measured from the horizontal axis of the SHCT-HE as 0◦, 30◦, 60◦, and 90◦. The results indicate that increasing the inclination angle enhances the coil Nusselt number (Nuc) and the effectiveness of SHCT-HE (ε); while, it decreases the coil pressure drop (ΔPc). Where, at coil Reynolds number of 15000, changing the orientation of the SHCT-HE from the horizontal to the vertical orientation improves the coil Nusselt number by 11%, 8.3%, and 7.5% for based water, Al2O3/water, and SiO2/water nanofluids with 0.1 vol%, respectively. Furthermore, at vertical orientation of heat exchanger and coil Reynolds number of 6000, utilizing Al2O3/water nanofluid with 0.1 vol% intensifies significantly the coil Nusselt number and the effectiveness than those for the based water by 35.7% and 35.5%, respectively. In addition, increasing the inclination angle up to 30◦ keeping the performance evaluation criterion (PEC) almost constant and more elevating into the vertical

orientation decreases the PEC. Using multiple regression analysis, empirical correlations are proposed to esti-

mate the coil Nusselt number (Nuc) for based water, Al2O3/water, and SiO2/water nanofluids as a function of Rec, θ, andϕ.

## Introduction

In the last decades, considerable developments have been achieved to improve the thermal performance and flow characteristics of heat exchangers [1,2]. The shell and helically coiled tube heat exchanger (SHCT-HE) is more preferable than traditional shell and tube heat exchanger, where it provides the compact size and can be used for high- temperature applications. The SHCT heat exchanger ensures high fluid mixing, so it has higher heat transfer coefficients than the straight tube heat exchanger [3]. The flow of a working fluid in a coiled tube gen- erates a centrifugal force forming a secondary flow that is responsible for enhancing the heat transfer characteristics; however, it increases the pressure drop compared with that of the straight tube. There are numerous engineering technologies that employ SHCT-HE such as refrigeration and air-conditioning systems, heat recovery processes and food processing, etc. [4,5].

Conventional fluids such as water and air have relatively low values of thermal conductivity that limits the heat transfer rates. Increasing the

thermal conductivity of the traditional heat transfer fluids can be maintained by dispersing nanoparticles into it without significant changes to their chemical and physical properties leading to improving the resulting heat transfer rate. In addition, increasing the volume concentration of the nanoparticles increases the viscosity of the nano- fluids causing its higher-pressure drop consequently higher pumping power [6,7]. A number of investigations were performed to study the thermos-physical properties of nanofluids to achieve a high thermal conductivity with relatively low viscosity [8,9,10,11]. Recent advances in nanomaterials and its measurements and modeling of thermo- physical properties were reviewed comprehensively by Qiu et al. [12]. In addition, Mahian et al. [13] overviewed in detail the fabrication, thermo-physical properties, and applications of nanofluids. As well, they discussed the different forces generated by nanofluid flow such as drag, lift, van der Waals, Brownian, thermophoretic, and electrostatic forces. Afterward, detailed descriptions of the essential physical models for nanofluid flows and heat transfer from single-phase to two-phase models were presented.

Kumar et al. [14] investigated experimentally the thermal

* Corresponding author.

E-mail address: Hussein_mag@eng.svu.edu.eg (H.M. Maghrabie).

https://doi.org/10.1016/j.applthermaleng.2020.116013

Received 5 March 2020; Received in revised form 2 September 2020; Accepted 4 September 2020

Available online 19 September 2020

1359-4311/© 2020 Elsevier Ltd. All rights reserved.

Abbreviations

PECPerformance Evaluation Criterion

SHCT-HE Shell and Helically Coiled Tube Heat Exchanger

inclination angle [degree] pressure drop [bar]

heat transfer effectiveness [-]

volume concentration of nanoparticles [%] dynamic viscosity [kg/m.s]

density [kg/m3]

time [sec]

ɵ

ΔP

ε ϕ μ ρ τ

Actual Average Bulk

Brownian motion based fluid

Coil

Reynolds number (Re = (ρuDh)/μ ) [–]

temperature [oC] volume flow rate [m3/s] velocity [m/s]

Greek letters

Effective freezing point Hot Hydraulic Cold

Inlet Inner maximum nanofluid outlet Outer

nanoparticle surface Shell

Tube

eff fr H

h C I

i max nf

O

o p s sh t

pitch [mm]

heat transfer rate [W]

Nusselt number (Nu = hDh/k) [–]

D [–]

i c

t,

.)

diameter of particle [nm]

convective heat transfer coefficient [W/m2.◦C] thermal conductivity [W/m.K]

Boltzmann’s constant [1.38066x10-23 J/K]

length [mm]

mass flow rate [kg/s] number of coil turns [–]

curvature ratio D /

Brownian diffusion coefficient [m2/s]

surface area [m2]

specific heat at constant pressure [kJ/kg.K] diameter [mm]

Nomenclature

A

Cp D DB DR D H K

Kb L

m˙ N

Nu P

Q˙

Re T

V˙

u

Subscripts act

avg b

B

bf c

performance and friction factor for a shell and coiled tube heat exchanger using Al2O3/water nanofluid with different volume concen- trations of 0.1 vol%, 0.4 vol%, and 0.8 vol% for laminar flow. The results indicated that the overall heat transfer coefficient, inner heat transfer coefficient, and inner Nusselt number for 0.8 vol% concentration were improved than those for water by 24%, 25%, and 28%, respectively. While, increasing the volume concentration of nanofluid increased the friction factor. Srinivas and Venu Vinod [15] investigated experimen- tally the heat transfer of a shell and coil heat exchanger using CuO/ water nanofluid with different weight concentrations i.e., 0.3 wt%, 0.6 wt%, 1 wt%, 1.5 wt%

and 2 wt%. The results indicated that using nanofluid improved the heat transfer compared to that for based water. This enhancement of heat transfer increased with increasing the Dean number and weight concentration of nanofluid. Khorasani et al. [16] studied experimentally the thermal performance of a helical tube using a spiral wire turbulator. The results revealed that the pitch and wire diameter had a considerable effect on the thermal performance of the helical tube.

Mirgolbabaei [17] investigated numerically the thermal perfor- mance of a vertical SHCT-HE considering the actual condition of con- jugate thermal boundary of the coil wall with varying the mass flow rate of shell-side, coil-to-tube diameter ratio, and coil pitch. The results showed that increasing the coil pitch lowered the effectiveness of SHCT- HE; however, changing the tube diameter had a modest effect on the effectiveness. As well, increasing the coil pitch up to a definite value decreased the heat transfer coefficient of the shell-side; whereas, further increasing of coil pitch enhanced the heat transfer coefficient of the shell-side. Kannadasan et al. [18] carried out an experimental study on the thermal performance and pressure drop of a helically coiled heat exchanger using CuO/water nanofluid for horizontal and vertical ori- entations of the heat exchanger. The results showed that increasing the Dean number and volume concentration of the nanofluid enhanced the Nusselt number (Nu) of the heat exchanger. Moreover, decreasing the

Dean number and increasing the volume concentration increased the friction factors. Furthermore, proposed correlations for computing the Nusselt number were developed for a helically coiled tube heat exchanger for a turbulent flow regime. Srinivas and Venu Vinod [19] performed an experimental study on heat transfer and effectiveness of a shell and helical coil heat exchanger using Al2O3/water, CuO/water, and TiO2/water nanofluids with different weight concentrations of 0.3 wt%, 0.6 wt%, 1 wt%, 1.5 wt%, and 2 wt%. The results indicated that the effectiveness of the heat exchanger using Al2O3/water, CuO/water, and TiO2/water nanofluids was greater than that of the based water by 30.37%, 32.7%, and 26.8%, respectively.

Elshazly et al. [20] performed an experimental investigation of the thermal performance of a horizontal shell and helical coil heat exchanger using γ-Al2O3/water nanofluid. Five helical coils were stud- ied with different values of coil torsions (pc/πDc) ranged from 0.0442 to 0.1348 under a turbulent flow regime. The volume concentration of γ-Al2O3 nanoparticles was varied from 0 vol% to 2 vol%. The results indicated that reducing the helical coil torsion improved the heat transfer rate, hence the thermal performance index as well as increased the friction factor of the helical coil (fc). Fule et al. [21] studied the heat transfer performance of a helical coil heat exchanger experimentally using CuO/water nanofluid with volume concentration varied from 0.1 vol% to 0.5 vol% and Re changed from 812 to 1895. The results indi- cated that using CuO/water nanofluid with 0.1 vol% and 0.5 vol% concentration, improved the heat transfer coefficient compared to the based fluid by 37.3% and 77.7%, respectively. In addition, increasing the Reynolds number from 812 to 1895 increased the heat transfer co- efficient by 4.4 times. Ferng et al. [22] investigated numerically the effect of the pitch size on fluid flow characteristics and the thermal performance of SHCT-HE. The results described reasonably the complicated fluid flow phenomena occurred in a SHCT-HE including the flow separation and acceleration within the shell side, the significant secondary flow in the coiled tube and the two wake vortices generated

4

1

7

5

2

3

6

5

| (1) Cooling unit | (2) Heating unit | (3) Holder | (4) SHCT-HE |
| --- | --- | --- | --- |
| (5) Pressure gauges | (6) Flowrate regulator | (7) Protractor |  |

Fig. 1. Real photo of the shell and hellicaly coiled tube heat exchanger (SHCT-HE) in the vertical orientation.

around the rear of coil.

Fig. 2. Schematic illustration of the experimental set-up in the horizontal orientation.

investigate the effect of fluid flow and geometrical parameters on the

Bhanvase et al. [23] investigated experimentally the thermal per- formance of a vertical coiled heat exchanger using PANI (polyaniline) nanofluid with volume concentration varied from 0.1 vol% to 0.5 vol%. The results revealed that the enhancements in the heat transfer coeffi- cient for 0.1 vol% and 0.5 vol% concentrations of PANI nanofibers rather than that of distilled water were 10.52% and 69.62%, respec- tively. Jamshidi et al. [24] performed a numerical study on the thermal performance and friction factor of helical coils using Al2O3/water nanofluid with volume fraction varied from 1% to 3% for laminar flow. Numerical simulation and Taguchi method were employed to

heat transfer rate and the pressure drop in the coils. As well, the design parameters of the helical coil with constant surface temperature using water and nanofluid were optimized. The results appeared the most important design parameters for the helical tube with fixed tube diam- eter and length were the diameter and pitch of the coil. Increasing the volume fraction and Re increased the Nu. While, the friction factor was increased by increasing the volume fraction and decreasing Re. Wang et al. [25] studied experimentally and numerically the performance of a SHCTHE with a trilobal tube. The results indicated that the strong ability to disturb the boundary layer improved the radial and circumferential

Fig. 3. Basic geometric parameters of the shell and hellicaly coiled tube heat exchanger.

Al2O3

SiO2

(a)

Al2O3

SiO2

Table 1

(b)

Fig. 4. Characteristics of Al2O3 and SiO2 nanoparticles (a) SEM images (b) TEM images.

heat exchanger; however, it decreased with increasing the mass flow rate. Akbaridoust et al. [27] carried out an experimental and numerical

Thermo-physical  properties  of nanoparticles.

Thermo-physical property	Al2O3	SiO2

Density, ρ [kg/m3]	5602.4	3427

Specific heat, cp [J/kg.K]	880	789

Thermal conductivity, k [W/m.K]	44.5	1.65

Average diameter of nanoparticle, dp [nm]	50

velocities near the tube wall. Moreover, the augmentation of the thermal performance of the helically trilobal tube was about 1.16–1.36 times compared with that of the helically coiled plain tube; however, the friction factor increased sharply by 0.96–1.10 times.

Bahrehmand and Abbassi [26] performed a numerical investigation of the heat transfer behavior and pressure drop of a shell and helical coil heat exchanger utilizing Al2O3/water nanofluid. The volume concen- tration of nanoparticle was varied from 0.1 vol% to 0.3 vol% and the coil Reynolds numbers (Rec) was varied from 9000 to 36,000 and that for the shell (Resh) was changed from 600 to 2600. The results indicated that the heat transfer rate and pressure drop were increased as a result of using nanofluid. In addition, increasing the tube and coil diameters and the volume concentration of nanofluid enhanced the effectiveness of the

investigation on the heat transfer characteristics and pressure drop for CuO/water nanofluid flowing through the coiled tubes at constant wall temperature with different curvature ratio. The working fluid regime was laminar steady-state flow and with a volume fraction of 0.1% and 0.2%. The results indicated that increasing the curvature ratio, Reynolds number and volume fraction of nanoparticle increased the heat transfer coefficient and the pressure drop. Moreover, the heat transfer for the helical tube was higher than that for the straight tube using based fluid. In addition, the performance index increased with increasing the cur- vature ratio.

Rakhsha et al. [28] carried out a numerical and experimental study concerning the thermal performance and pressure drop of CuO/water nanofluid with a 0.1 vol% concentration flowing through a horizontal helically coiled tube. The results indicated that increasing the Reynolds number and the curvature ratio of the coiled tube increased the pressure drop and the heat transfer coefficient. Also according to the experi- mental results, using nanofluid increased the pressure drop and enhanced the heat transfer coefficient rather than those for the based fluid by 16–17% and 14–16%, respectively. Furthermore, the heat transfer coefficient and pressure drop increased with increasing the

Fig. 5. Thermo-physical properties of based water and AL2O3/water and SiO2/water nanofluids with different volume concentrations such as (a) density (b) specific heat (c) thermal conductivity.

curvature ratio and Reynolds number. Mahmoudi et al. [29] carried out an experimental and numerical study concerning the heat transfer behavior and the pressure drop of a horizontal coiled tube using TiO2/ water nanofluid. The effects of the curvature ratio and volume concen- tration of nanofluid with varying the Reynolds number from 3000 to 18,000 were studied. The results indicated that using nanofluid rather than based water enhanced the heat transfer as well as increased the pressure drop. Furthermore, proposed correlations to calculate the Nusselt number and friction factor were presented as functions of

Reynolds number, Prandtl number, volume concentration, and curva- ture ratio under constant wall temperature of a coil for laminar as well as turbulent flow regimes.

The recent advances on the conventional shell and helically coiled tube heat exchanger (SHCT-HE) were focused to intensify the heat transfer that is might be accompanied by increasing the pressure drop. As well as, the previous studies examined the different operating and design parameters of the SHCT-HE on either horizontal orientation or vertical orientation. To the authors’ knowledge, investigating the

Table 2

The uncertainties of the experimental measurements.

Variable	Uncertainty value (%)

Temperature, t	± 0.39%

Inclination angle, ɵ	± 1.15%

Reynolds number, Rec	± 2.73%

Nusselt Number, Nuc	± 3.24%

Effectiveness, ε	± 2.74%

Pressure drop, ΔPc	± 3.1%

## Experimental apparatuses and procedure

The real photo of the experimental set-up with the vertical orienta- tion of SHCT-HE is shown in Fig. 1; while, its schematic diagram in the horizontal orientation of SHCT-HE is shown in Fig. 2. The experimental set-up consists of SHCT-HE, cooling unit of GUNT WL 110.20 water chiller, heating unit of GUNT WL 110 service unit, and holder. The heating and cooling units supply the SHCT-HE with the required hot and cold working fluids, respectively. The heating and cooling units are

Fig. 6. Coil Nusselt number (Nuc) versus Rec at vertical orientation of SHCT-HE for different volume concentrations of (a) Al2O3/water (b) SiO2/water nanofluids.

thermal performance and the pressure drop of the SHCT-HE with vari- able orientation was not recorded in the available literature. Therefore, the aim of the present implementation is to assess the heat transfer and the pressure drop of the SHCT-HE with varying the inclination angle utilizing Al2O3/water and SiO2/water nanofluids flowing inside the helical coil. In the present study, the performance of SHCT-HE is eval- uated using the following indicators: coil Nusselt number (Nuc), effec- tiveness (ε), and coil pressure drop (ΔPc). In order to assess comprehensively the performance of SHCT-HE, the heat transfer enhancement is accompanied by the pressure drop, so the performance evaluation criterion (PEC) is studied. Finally, the multiple regression analysis is employed to obtain empirical equations estimating the coil Nusselt number (Nuc) for each working fluid.

provided with water storage tanks, pumps, displays, and appropriate control systems to regulate the inlet temperatures and flow rates of hot and cold working fluids. The basic geometric parameters of SHCT-HE are illustrated schematically in Fig. 3. The helically coiled tube that is made from a copper tube with 27 number of turns (N) has an inner diameter (Dt,i) and outer diameter (Dt,o) of 4.35 mm and 6.35 mm, respectively. The shell that is fabricated from PVC pipe with a 107 mm inner diameter (Dsh,i) and 114 mm outer diameter (Dsh,o), is insulated from the surrounding using fiberglass wool insulation with a thermal conductivity of 0.0432 W/m.K. The cold water flows through the shell with a constant Reynolds number (Resh) of 900. While, the hot fluids such as based water, Al2O3/water, and SiO2/water nanofluids with volume concentrations of 0.1 vol%, 0.2 vol%, and 0.3 vol% flow through the helically coiled tube with a Reynolds number (Rec) varied from 6000 to 15000. In the current study, the experiments are conducted in the

counter-flow configuration, where the hot fluids flow from up to down. The hot and cold fluids are pumped with specified flow rates into closed cycles to the SHCT-HE at the desired inlet temperatures. For each experiment, the inlet temperatures of cold fluid (TI,C) and hot fluid (TI,

H) are constant at 15 ◦C and 60 ◦C, respectively. The flow rates, the inlet

and outlet temperatures of both helically coiled tube and shell and be- sides the coil surface temperatures (T1, T2, T3, and T4) are recorded at the steady-state operation. Constructed holes with a depth up to a half- millimeter are drilled into the tube wall to insert the thermocouple junction into the wall. After inserting the thermocouple junction into the tube wall, it was tightly covered by a metallic strip, so that it is kept in good contact with the wall surface by a special glue. Then, it is tightly covered by a Teflon tape to avoid the water penetration to the junction even at the maximum operating temperature of 60 ◦C for the hot water flowing through the coiled tube. This assembly is achieved to ensure that the thermocouple junctions are precisely secured and to eliminate the disturbing of the thermocouple readings. As well as, to avoid any fluid disturbance  coming in contact with the thermocouple junctions.  Thus,

sufficient care is taken while attaching and fixing the thermocouple junctions on the surface of the tube wall to reduce the uncertainties in the wall temperature measurements. In addition, the inlet and outlet pressures for the helically coiled tube are registered. The experimental results of each parameter are recorded for six runs to compute its average value. The orientation of SHCT-HE is changed from the hori- zontal orientation (0◦) to the vertical orientation (90◦) manually by the aid of a mechanical holder. For each orientation, the temperatures and

pressures at the inlet and outlet of the helically coiled tube and the shell and the surface temperatures of the coil are recorded.

## Materials and preparation of nanofluids

SiO2/water nanofluids are prepared with different volume concentra- tions of 0.1 vol%, 0.2 vol%, and 0.3 vol%. The weight of Al2O3 and SiO2 nanoparticles, required for the desired volume concentrations, is measured by the analytical balance. The nanofluids are stirring by a magnetic stirrer of DRAGON LAB MS-S and then exposed to Ultrasonic Homogenizer of BIOLOGICS, Inc. Model 3000 for 4 h to be stable and homogeneous. In the present study, after ultrasonication process, the sedimentation of nanoparticles is observed. Experiments are carried out where the prepared nanofluids with different volume concentrations are used immediately to prevent the sedimentation of nanoparticles. There are no observations regarding the changes in sedimentation and con- centration of nanoparticles during the experiments. Any tendency of nanoparticles sedimentation is examined accurately by measuring the densities of nanofluid samples from the hot tank of the heating unit.

## Thermo-physical properties of nanofluids

The thermo-physical properties of nanoparticles have significate ef- fects on the thermal characteristics of nanofluids, consequently, it im- pacts the heat exchanger performance. Thermo-physical properties of Al2O3 and SiO2 nanoparticles such as density, specific heat, and thermal conductivity that are tested at the National Research Center, Cairo, Egypt, are presented in Table 1. The thermo-physical properties of AL2O3/water and SiO2/water nanofluids are estimated using various correlations, where the density of nanofluid (ρnf ) is calculated from the

following equation [12,30]

ρnf  = ϕρp + ρbf (1 — ϕ)	(1)

The specific heat of Al2O3/water and SiO2/water nanofluids (CP,nf) is calculated as below [30,31]

The average size of Al2O3 and SiO2 nanoparticle is 50 nm with a

CP nf = ϕρp CP,p + ρbf CP,bf (1 — ϕ)

(2)

purity of 95% are employed to study the performance of SHCT-HE. Fig. 4 illustrates the scanning electron microscope (SEM) and transmission

,	ρnf

The effective dynamic viscosity of nanofluids (μnf ) is estimated from

electron microscope (TEM) images indicating the morphology charac- teristics of Al2O3 and SiO2 nanoparticles that are achieved in the Na-

the following empirical relation [32,33]

tional Research Center, Cairo, Egypt. In the present study, proper mixing

μnf	 	1

and  sonication  processes  are  achieved  to  maintain  the   appropriate

dispersion of nanoparticles into the based fluid. The Al2O3/water and

μbf   = 1 — 34.87ϕ1.03 .dp/dbf )—0.3	(3)

Fig. 7. Coil Nusselt number (Nuc) versus inclination angle of SHCT-HE at Rec = 15000 for based water, Al2O3/water, and SiO2/water nanofluids with different volume concentrations.

The effective thermal conductivity of nanofluids (knf ) is estimated from the following equations [26,32,34,35]

τ	dp 2

=

=

6

πμbf

dp 3

(7)

knf

0 66

0 4       0 66 (Tnf  + 273)10 ( kp )0.03

DB	2Kb(Tnf + 273)

kbf

= 1 + 4.4ϕ .

ReB . Pr .

Tfr +

273

kbf

(4)

where DB

is the Brownian diffusion coefficient in m2/s and Kbis the

where ReB is the Reynolds number of Brownian motion, which is calculated as below

Boltzmann’s constant that equals 1.38066*10—23 J/K.

So, the Reynolds number of the Brownian motion for a nanoparticle will be

ReB = ρbf uBdp

μbf

(5)

ReB

2ρbf Kb(Tnf + 273)

πμbf 2 dp

(8)

where uB is the mean Brownian velocity in m/s.

=

The Brownian velocity of a nanoparticle that is defined as the ratio between the diameter of nanoparticle (dp) and the time (τ) taken by the nanoparticle to move a distance equal to its diameter, can be evaluated as follow

(6)

Fig. 5 illustrates the thermo-physical such as density, specific heat, and thermal conductivity for the based water and AL2O3/water and SiO2/water nanofluids with different volume concentrations versus its operating temperature. It is clear that the density decreases with increasing  the  temperature.  As  well  as,  the  density  of Al2O3/water

nanofluid is higher than that of SiO2/water nanofluid as a result of the

d

p

uB = τ =

2Kb(Tnf + 273)

πμbf dp2

nanoparticles of Al2O3 have a higher density than that of SiO2 nano- particles. In addition, the density for both Al2O3/water and SiO2/water

where, the time (τ) that is required to move the nanoparticle, can be calculated according to the relation presented by Keblinski et al. [33].

nanofluids are higher than that for based water at different tempera- tures. In addition, the specific heat decreases with increasing the tem- perature up to 35 ◦C and it increases with further increasing in temperature. The specific heat of Al2O3/water nanofluid is lower than that of SiO2/water nanofluid and both are lower than that for the based

Fig. 8. Heat exchanger effectiveness (ε) versus Rec at vertical orientation of SHCT-HE for different nanoparticles volume concentrations of (a) Al2O3/water (b) SiO2/ water nanofluids.

water at different temperatures. On the other hand, the thermal con- ductivity of Al2O3/water nanofluid is higher than that of the SiO2/water and both are greater than that of the based water.

Ts,avg = (T1+T2 + T3+T4)/4	(11)

The convection heat transfer coefficient of the helical coil (hc) is calculated by

## Data reduction

The performance of the shell and helically coiled tube heat

hc =

[m˙HC

p,H

.TI,H —

TO,H ) ]

(12)

exchanger (SHCTHE) is investigated using different nanofluids taking into consideration the effect of inclination angle (ɵ). The convective heat transfers between the hot and cold fluids can be estimated using the mass flow rate of each fluid as well as its inlet and outlet temperatures and the heat transfer surface area. The hot fluids pass through the he- lically coiled tube; while, the cold distilled water flows through the shell. In the present study, the coil Nusselt number (Nuc), effectiveness of

SHCT-HE (ε), coil pressure drop (ΔPc , as well as the performance

)

evaluation criterion (PEC) are evaluated.

  - Heat transfer

The convection heat transfer of the coiled tube is expressed using Newton’s law of cooling and the energy equation is shown below [36]

As Tb,avg — Ts,avg

[  .	) ]

So, the Nusselt Number of the helically coiled tube (Nuc) can be expressed as [36]

..	)/ )

Nuc  =    hDt,i   k  c	(13)

In the present study, the knf and Cp are calculated at the average bulk temperature. In addition, the Reynolds number for the shell or helically coiled tube (Re) is expressed as follow

Re = (ρuDh)/μ	(14)

where, ρ is the density and μ is the dynamic viscosity calculated at the average bulk fluid temperature and Dh is the hydraulic diameter where its value for the coiled tube equals to its inner diameter; however, the hydraulic diameter for the shell can be calculated from the following

equation [37]

Q˙c  = hc As .Tb,avg — Ts,avg ) = m˙H Cp,H .TI,H  — TO,H )	(9)

π Dsh,i 2 Lsh

—

π Dt,o 2 Lt

= 4

where As is the surface area of the helically coiled tube in m2

and Tb,avgis

Dh sh  = 4	shellsidevolume

[( .	)

4

) ( .

4

)	) ]

the average bulk temperature of the hot fluid in

C that is calculated by

,	surfacecontactwiththefluid

[.πDsh i Lsh ) + .πDt o Lt ) ]

◦

Tb,avg = .TI.H + TO,H )/2	(10)

,	,

so, the hydraulic diameter of the shell equals to80mm.

(15)

where Ts,avg is the average surface temperature of the helically coiled

tube

Furthermore, the velocity of the fluid through the shell (ush) is

calculated by

The average coil surface temperature is estimated by measuring the

V˙sh

=

4

h,sh

u

(16)

four local temperatures (as described in Fig. 2) using Eqn. (11). As well

as, it is evaluated using the numerical trapezoidal rule in the interval

sh	π.D )2

[x4, x1] that is divided into n subintervals with equal spacing. The  re- sults show that the error in computing Ts,avg using the two methods with varying the coil Reynolds number (Rec) and inclination angle (ɵ) for different working fluids i.e., based water, Al2O3/water, and SiO2/water nanofluids is less than one percentage.

  - Heat exchanger effectiveness (ε)

The heat exchanger effectiveness can be expressed as [36]

Fig. 9. Effectiveness of heat exchanger (ε) versus inclination angle of SHCT-HE at Rec = 15000 for based water, Al2O3/water, and SiO2/water nanofluids with different volume concentrations.

ε = Q˙act /Q˙max	(17)

where; Q˙act  and Q˙max  are the actual and maximum heat transfer rates in Watt, respectively.

Through the present implementation, the Q˙act   is determined as the average heat transfer rate of the hot and cold working mediums, and it is calculated from the following equation

Q˙act  = Q˙avg  = (Q˙H  + Q˙C )/2	(18)

While, for the counter-flow heat exchanger, the maximum heat transfer (Q˙max ) is calculated from

Q˙max  = Cp,H *m˙H.TI,H — TI,C)	(19)

  - Coil pressure drop (ΔPc)

Moreover, the pressure drop of the hot fluids due to passing through the helically coiled tube (ΔPc that equals to the pressure difference between the inlet and outlet of the coil, can be estimated using the following relation

)

ΔPc = PI,c — PO,c	(20)

where ΔPc is the coil pressure drop in bar, PI,c and PO,c are the inlet and outlet pressures to/from the helically coiled tube in bar.

  - Performance evaluation criterion (PEC)

In the present investigation, the performance evaluation criterion (PEC) is used to evaluate the performance of the heat exchanger using Al2O3/water and SiO2/water nanofluids and compared to the corre- sponding value for the based water. The performance evaluation crite- rion accompanies between the heat transfer enhancement and the pressure drop of the SHCT-HE. It is utilized to assess the heat transfer enhancement of the SHCT-HE at the same pumping power, and it can be calculated from the following equation [18,38,39]

nanoparticles on the coil Nusselt number (Nuc) with varying the coil Reynolds Number (Rec) at the vertical orientation of the SHCT-HE. It is indicated that using Al2O3/water and SiO2/water nanofluids enhances the Nuc greater than that of the based water. At Rec of 6000, the im- provements of Nuc due to using Al2O3/water and SiO2/water nanofluids with 0.1 vol% concentration of nanoparticles compared with that of the based water are 35.7% and 16.2%, respectively. Furthermore, at Rec equals 15000, the values of Nuc for Al2O3/water and SiO2/water nanofluids with 0.3 vol% concentration of nanoparticles are higher than that for 0.1 vol% concentration by 35.5% and 34.5%, respectively. In addition, increasing the Rec from 6000 to 15,000 enhances the Nuc by 62%, 96%, and 67.9% for the based water and 0.3 vol% concentration of Al2O3/water and SiO2/water nanofluids, respectively. This is due to, the values of thermal conductivity of Al2O3/water and SiO2/water nano- fluids are higher than that of the based water. In addition, increasing the volume concentration enhances the performance of the heat transfer process [31,41]. Moreover, the superior heat transfer due to using nanofluids rather than based water is due to various generated forces as a result of nanofluid flow such as drag, lift, van der Waals, Brownian, thermophoretic, and electrostatic forces [13].

Fig. 7 shows the coil Nusselt number (Nuc) for based water, Al2O3/

water and SiO2/water nanofluids with varying the volume concentra- tion versus the inclination angle (ɵ) from the horizontal orientation (0◦) to the vertical orientation (90◦) at Rec of 15000. It is observed that changing the inclination angle of the SHCT-HE from the horizontal to the vertical orientation enhances the Nuc by almost 11%, 8.3%, and 7.5% for based water, Al2O3/water, and SiO2/water nanofluids with 0.1 vol% concentration, respectively. At the vertical orientation of the SHCT-HE, the Nuc due to utilizing Al2O3/water nanofluid with 0.3 vol% concentration of nanoparticles is higher than that of SiO2/water nano- fluid at the same concentration by 26.6%. This due to the Al2O3 nano- particles have a higher thermal conductivity than that of SiO2 nanoparticles, resulting to higher thermal conductivity of Al2O3/water than that of SiO2/water nanofluid. Further, as a result of adding nano- particles into the based water, the coil Nusselt number is increased due to the higher thermal conductivity of the nanofluids compared to that of

the based water, forces acting on suspended nanoparticles in a based

fluid by different sources, as well as the formation of the secondary flow

)0.33

PEC = (D  )0.003[.

R

ΔP

Nunf /Nubf

nf

/ΔPbf

]	(21)

due to the migration of nanoparticles leading to improving the heat

transfer [13,17,42,43,44].

where DR is the curvature ratio that is defined as the ratio of inner tube diameter (Dt,i) to the mean coil diameter (Dc).

## Uncertainty analysis

The uncertainty analysis is required to assess the uncertainty in all measurements through the quantification of uncertainties in the rele- vant variables and therefore assessing the confidence in the results to be reliable. The uncertainties for all temperature (T) measurements at the inlet and outlet of the helically coiled tube and the shell as well as the uncertainty of the inclination angle (ɵ) of the SHCT-HE are evaluated. In addition, the uncertainties of the coil Reynolds number (Rec) and the coil pressure drop (ΔPc) are estimated. Therefore, the uncertainty of the related parameter such as coil Nusselt number (Nuc) and the effective- ness of SHCT-HE (ε) are calculated. The uncertainty for the experimental parameter is estimated using the based water as a working fluid through the helically coil for the horizontal orientation of the SHCT-HE based on the methodology indicated in [40]. The results of the uncertainty analysis for different parameters are listed in Table 2.

## Experimental results and discussions

  - Coil Nusselt number (Nuc)

Fig. 6 illustrates the effect of the volume concentration of

  - Effectiveness of SHCT-HE (ε)

Fig. 8 presents the effect of the volume concentration of the nano- particles on the effectiveness of heat exchanger (ε) against Rec varied from 6000 to 15,000 for the vertical orientation of SHCT-HE. It is demonstrated that the utilization of Al2O3/water and SiO2/water nanofluids enhances the effectiveness of the SHCT-HE compared with that of based water. At Rec = 6000 the effectiveness of the SHCT-HE using Al2O3/water and SiO2/water nanofluids with 0.1 vol% concen- tration is higher than that of the based water by 35.5% and 15.6%, respectively. In addition, the effectiveness of SHCT-HE increases with increasing the volume concentration of nanoparticles. Where, at Rec = 15000, the effectiveness of SHCT-HE using Al2O3/water and SiO2/water nanofluids with 0.3 vol% concentration is higher than those of nano- fluids with 0.1 vol% concentration by 25.5% and 31%, respectively. Utilizing nanofluids with high volume concentration increases the heat transfer rate, which causes an increase in the effectiveness of the SHCT- HE [21,23]. The effectiveness of the SHCT-HE (ε) against the inclination angle (ɵ) for the based water, Al2O3/water and SiO2/water nanofluids with different volume concentrations of nanoparticles at Rec of 15,000 is illustrated in Fig. 9. At ɵ=90◦, the effectiveness of the SHCT-HE using

0.3 vol% of Al2O3/water nanofluid is higher than that of SiO2/water

nanofluid by 12.6%. The effectiveness of the SHCT-HE using Al2O3/ water nanofluid is enhanced more than that of SiO2/water. Furthermore, it is noticed that increasing the inclination angle of the SHCT-HE from

Fig. 10. Coil pressure drop (ΔPc) versus Rec for a vertical orientation of SHCT-HE for different volume concentrations of (a) Al2O3/water (b) SiO2/water nanofluids.

0◦ to 90◦ improves the effectiveness of the SHCT-HE by 23%, 8.5%, and 6.5% for the based water, Al2O3/water, and SiO2/water nanofluids with

0.1 vol% concentration, respectively.

  - Coil pressure drop (Δpc)

Fig. 10 represents the effect of the volume concentration of nano- particles on the pressure drop through the coiled tube (ΔPc) with varying the Rec from 6000 to 15,000 for the vertical orientation of SHCT-HE (ɵ=90◦). It is observed that the ΔPc increases with increasing the vol- ume concentration of the nanoparticles. Where, at Rec = 15000, the ΔPc through the coil tube of the SHCT-HE using Al2O3/water and SiO2/water nanofluids with 0.1 vol% concentration increases by 25% and 36.1% than that of the based water, respectively. Furthermore, at Rec = 15000, the ΔPc increases as a result of increasing the volume concentration of nanoparticles from 0.1 vol% to 0.3 vol% by almost 11% and 10% for Al2O3/water and SiO2/water nanofluids, respectively. The dynamic viscosity has a considerable effect on the pressure drop through the coil of the heat exchanger rather than the density, velocity, and concentra- tion of nanoparticles. This effect is significant with increasing the vol- ume concentration of nanoparticles [34]. Where, the based water has a lower dynamic viscosity than nanofluids so it has the lowest value of ΔPc.

Fig. 11 indicates the pressure drop through the helical coil (ΔPc) versus the inclination angle (ɵ) at Rec of 15,000 for the based water,

Al2O3/water and SiO2/water nanofluids with different volume concen- trations. It is observed that the SiO2/water nanofluid causes a higher ΔPc than that of Al2O3/water nanofluid. Where, for the vertical orientation of SHCT-HE, the ΔPc of the SiO2/water nanofluid with 0.3 vol% con- centration of nanoparticles is higher than that of the Al2O3/water nanofluid by 8%. Moreover, the ΔPc for the vertical orientation of SHCT- HE is lower than that of the horizontal orientation by 11.8% and 10.9% for Al2O3/water and SiO2/water nanofluids with 0.1 vol% concentration of nanoparticles, respectively. Regardless of the effect of the dynamic viscosity of Al2O3/water and SiO2/water nanofluids, the SiO2/water nanofluid has a lower density compared with that of Al2O3/water nanofluid, so it has a higher velocity causing higher ΔPc. The pressure drop through the coil may be pronounced when the centrifugal force is less than or equal to the gravity force and therefore the frictional pres- sure drop may differ as well. On the other hand, the gravity influences the distribution of the secondary flow which is developed along the circumference direction of the coiled tube and is considered as one of the major variations which increase considerably the frictional pressure drop [17,45,46].

  - Performance evaluation criterion (PEC)

Fig. 12 indicates the performance evaluation criterion (PEC) of the SHCT-HE as presented in Eqn. (21) at the vertical orientation of SHCT- HE versus Rec for Al2O3/water and SiO2/water nanofluids with different

Fig. 11. Coil pressure drop (ΔPc) versus inclination angle of SHCT-HE at Rec = 15000 for based water, Al2O3/water and SiO2/water nanofluids with different volume concentrations.

volume concentrations. It is illustrated that the PEC increases with increasing the Rec and volume concentration. For Al2O3/water nano- fluid at Rec 15000, the values of PEC are 1.27, 1.41, and 1.67 for volume concentration of 0.1 vol%, 0.2 vol%, and 0.3 vol%, respectively. The improvement in the convective heat transfer caused due to using Al2O3/water nanofluid is higher than the rising in the ΔPc; therefore, the PEC is higher than unity. On the other hand, PEC for SiO2/water nanofluid with 0.1 vol% concentration is lower than unity this implies that the enhancement in the convective heat transfer is lower than the rise in the ΔPc. While, for high values of volume concentration of SiO2/ water nanofluids i.e., 0.2 vol% and 0.3 vol% the PEC equals 1.11 and 1.28, respectively. Moreover, at Rec 15000, increasing the volume concentration of nanoparticles from 0.1 vol% to 0.3 vol% enhances the PEC by 31.5% and 30.6% for Al2O3/water and SiO2/water nanofluids, respectively. Furthermore, increasing the Rec from 6000 to 15,000 has a

=

=

of the coil Reynolds numbers (Rec) and inclination angle of the SHCT-HE (θ) (Eqn. (22)). As well as, those for the Al2O3/water and SiO2/water nanofluids as a function of the coil Reynolds numbers (Rec), volume concentrations of nanoparticles (ϕ), and inclination angle of the SHCT- HE (θ) in Eqns. (23) and (24), respectively. The inclination angle of SHCT-HE (θ) presented in these empirical correlations are in radian

degree and taken in the range of (0.017 θ rad. 1.571).

≤  (	) ≤

For based water:

Nuc  = 0.0347(Rec)0.578 (θ)0.0206	(22)

For Al2O3/water nanofluid:

Nuc  = 0.0344(Rec)0.681 (θ)0.0144 (ϕ)0.2567	(23)

For SiO2/water nanofluid:

slight effect on the PEC of the SHCT-HE using SiO2/water nanofluid; while, it has a significant effect on the PEC of the SHCT-HE using Al2O3/ water nanofluid, particularly for higher values of volume concentration. Fig. 13 illustrates the performance evaluation criterion (PEC) of the SHCT-HE using Al2O3/water and SiO2/water nanofluids with different volume concentrations versus the inclination angle (ɵ) at Rec of 15000. It is cleared that the PEC of the Al2O3/water nanofluid is higher than that of SiO2/water nanofluid at the same volume concentration and it

decreases with increasing the inclination angle. For the vertical orien- tation of SHCT-HE (ɵ=90◦), the PEC of Al2O3/water nanofluid with 0.3 vol% concentration is greater than that of SiO2/water nanofluid with the same concentration by 18.5%. Moreover, the PEC of Al2O3/water nanofluid is higher than that of SiO2/water nanofluid for different vol- ume concentrations as a result of using Al2O3/water that enhances the convective heat transfer to extend higher than that of SiO2/water. As well as, the SiO2 nanoparticles raises the ΔPc than that of Al2O3 nano- particles. Further, changing the inclination angle of SHCT-HE from 0◦ up to 30◦ keeping the PEC almost constant for all hot working fluids; while, increasing the inclination angle more than 30◦ decreases the PEC as a result of the degree of the heat transfer enhancement relative to the elevating of the coil pressure drop.

Finally, based on the present obtained experimental results, the multiple regression analysis is utilized to obtain empirical correlations to estimate the coil Nusselt number (Nuc) for based water as a function

Nuc  = 0.062(Rec)0.596 (θ)0.0168 (ϕ)0.2522	(24)

The above correlations are applicable for the investigated values of the coil and shell Reynolds numbers (RecandResh), and the tested values of the volume concentration of nanoparticles of Al2O3 and SiO2 (ϕ) for the specified values of the design parameters of SHCT-HE shown in Fig. 3. The results of the regression analysis that show the significant

effect of the examined parameters (Rec, θ, andϕ) on the thermal perfor-

mance of the SHCT-HE, are presented in Table 3. The values of the standard errors for the obtained empirical equations are within acceptable limits hence the variation of calculated values of Nucare in a good agreement with its measurable values as shown in Fig. 14. It is observed that the maximum deviation between the estimated values of Nuc using equations (22–24) with that of the experimental values is almost within ± 3%.

  - Validation of the present work

In order to validate the present work, a comparison between the experimental and calculated results of the coil Nusselt number (Nuc) of the present study with those of Elshazly et al. [20] and Salem et al. [37] is carried out and illustrated in Fig. 15. The results of the coil Nusselt number (Nuc) in the current implementation due to using based water that is calculated by Eqn. (22) and due to using Al2O3/water nanofluid

Fig. 12. Performance evaluation criterion (PEC) versus Rec at vertical orientation of SHCT-HE for different volume concentrations of (a) Al2O3/water (b) SiO2/ water nanofluids.

with 0.3 vol% volume concentration that is estimated using Eqn. (23) are compared with those using based water in [37] and γ-Al2O3/water nanofluid in [20], respectively. The comparison is carried out for the horizontal orientation of the SHCT-HE and the coil Reynolds number (Rec) is examined in the range from 6000 to 15000. The results of the comparison indicate that the coil Nusselt number (Nuc) for the present and previous studies increase with increasing the coil Reynolds number (Rec) with the same trend. On the other hand, the values of the coil Nusselt number (Nuc) of the present study are lower than those of the previous study and this deviation is due to the differences in the design parameters.

## Conclusions

The present investigation is carried out experimentally to study the heat transfer and pressure drop of the shell and helically coiled tube heat exchanger (SHCT-HE) with varying the inclination angle using based water, Al2O3/water and SiO2/water nanofluids as working fluids under a wide range of coil Reynolds number (Rec) from 6000 to 15000. The inclination angle (θ) is measured from the horizontal axis of the heat exchanger and its values are 0◦, 30◦, 60◦, and 90◦. In the present study,

the coil Nusselt number (Nuc), heat exchanger effectiveness (ε), coil pressure drop (ΔPc), and performance evaluation criterion (PEC) are estimated to assess the performance of SHCT-HE. The results reveal that the inclination angle of the SHCT-HE significantly influences on its thermal performance and pressure drop using Al2O3/water and SiO2/ water nanofluids and the following conclusions are summarized as below:

At vertical orientation of SHCT-HE and at coil Reynolds number of 6000, the enhancements in the coil Nusselt number and the effec- tiveness of heat exchanger due to utilizing 0.1 vol% Al2O3/water nanofluid compared to those of the based water are 35.7% and 35.5%, respectively.

•

For the coil Reynolds number of 15000, changing the orientation of the SHCT-HE from the horizontal to the vertical orientation enhances the coil Nusselt number for based water, Al2O3/water, and SiO2/ water nanofluids with 0.1 vol% concentration by almost 11%, 8.3%, and 7.5%, respectively.

•

For the vertical orientation of the SHCT-HE at coil Reynolds number of 6000, the coil Nusselt number and the effectiveness of SHCT-HE

•

Fig. 13. Performance evaluation criterion (PEC) versus inclination angle of SHCT-HE at Rec = 15000 for Al2O3/water and SiO2/water nanofluids with different volume concentrations.

Table 3

Results of the regression  statistics.

|  | Eqn. (22) | Eqn. (23) | Eqn. (24) |
| --- | --- | --- | --- |
| Multiple R | 0.993976355 | 0.992915594 | 0.991057 |
| R Square | 0.987988994 | 0.985881376 | 0.982195 |
| Adjusted R Square | 0.986845089 | 0.985258496 | 0.981409 |
| Standard Error | 0.021911851 | 0.030253979 | 0.030773 |
| Observations | 24 | 72 | 72 |

- At coil Reynolds number of 15000, the effectiveness of the SHCT-HE using Al2O3/water and SiO2/water nanofluids with 0.3 vol% con- centration are higher than those of 0.1 vol% concentration by 25.5% and 31%, respectively.

Changing the inclination angle of the SHCT-HE from 0◦  to 90◦  en-

•

hances the effectiveness by 23%, 8.5%, and 6.5% for based water and

0.1 vol% Al2O3/water and SiO2/water nanofluids, respectively.

- For the vertical orientation of SHCT-HE at coil Reynolds number of 15000, the coil pressure drop of SiO2/water nanofluid with 0.3 vol%

Fig. 14. Comparison between experimental and estimated values of Nuc for different working fluids.

are higher than those for the horizontal orientation by 11.3% and 13.1% for 0.1 vol% Al2O3/water nanofluid.

concentration of nanoparticles is higher than that of Al2O3/water nanofluid by 8%.

Fig. 15. Comparison between the coil Nusselt number (Nuc) of the present study and those of the previous works.

At coil Reynolds number of 15000, the coil pressure drop for the vertical orientation of the SHCT-HE is lower than that of the hori- zontal orientation by 11.8% and 10.9% for 0.1 vol% Al2O3/water and 0.1 vol% SiO2/water nanofluids, respectively.

•

At coil Reynolds number of 15,000 for the vertical orientation of the SHCT-HE, increasing the volume concentration of the nanoparticles of Al2O3/water from 0.1 vol% to 0.3 vol% increases the performance evaluation criterion by 31.5%.

•

  - For the vertical orientation of the SHCT-HE, the performance eval-

uation criterion of the SHCT-HE using Al2O3/water nanofluid with

0.3 vol% concentration is greater than that of SiO2/water nanofluid by 18.5%.

Changing  the  inclination  angle  of  SHCT-HE  from  0◦  up  to 30◦

•

maintains  almost  constant  performance  evaluation  criterion  and

Therm. Sci. 107 (2016) 196–208, https://doi.org/10.1016/j. ijthermalsci.2016.04.010.

- R. Saidur, K.Y. Leong, H.A. Mohammad, A review on applications and challenges of nanofluids, Renew. Sustain. Energy Rev. 15 (2011) 1646–1668, https://doi.org/ 10.1016/j.rser.2010.11.035.

- P.C.M. Kumar, M. Chandrasekar, A review on helically coiled tube heat exchanger using nanofluids, Mater. Today. Proc. 21 (2020) 137–141.

- S.K. Das, U.S. Choi, W. Yu, T. Pradeep, Nanofluids: Science and Technology, John Wiley & Sons Inc., Hoboken, New Jersey, 2007.

- J.A. Eastman, U.S. Choi, S. Li, L.J. Thompson, S. Lee, Enhanced Thermal Conductivity through the Development of Nanofluids, in: Symp. V – Nanophase Nanocomposite Mater. II, 1996: p. 3. doi:10.1557/PROC-457-3.

- A.M. Fsadni, J.P.M. Whitty, A.A. Adeniyi, J. Simo, H.L. Brooks, A review on the application of nanofluids in coiled tube heat exchangers, in Micro and Nanomanufacturing Volume II, M. J. Jackson and W. Ahmed, Eds., Springer International Publishing AG, 2018. doi:10.1007/978-3-319-67132-1.

- B. Sunden, Z. Wu, in: V. Bianco, O. Manca, S. Nardini, K. Vafai (Eds.), Heat Transfer Enhancement with Nanofluids, CRC Press, Taylor & Francis Group, New York,

more elevating the SHCT-HE in the vertical orientation lowers the

2015.

˙

performance evaluation criterion.

  - Finally, empirical correlations are developed using multiple regres- sion analysis to compute the coil Nusselt number (Nuc) for based water, Al2O3/water and SiO2/water nanofluids as a function of examined parameters of Rec, θ, andϕ with an average estimated error

of ± 3%.

## Declaration of Competing Interest

The authors declare that they have no known competing financial interests or personal relationships that could have appeared to influence the work reported in this paper.

## References

- T. Kuppan, Heat Exchanger Design Handbook, 2nd ed, Marcel Dekker , New York, 2013. doi:10.1017/CBO9781107415324.004.

- G. Huminic, A. Huminic, Heat transfer and flow characteristics of conventional fluids and nano fluids in curved tubes: a review, Renew. Sustain. Energy Rev. 58 (2016) 1327–1347, https://doi.org/10.1016/j.rser.2015.12.230.

- D.G. Prabhanjan, G.S.V. Raghavan, T.J. Rennie, Comparison of heat transfer rates between a straight tube heat exchanger and a helically coiled heat exchanger, Int. Commun. Heat Mass Transf. 29 (2002) 185–191, https://doi.org/10.1016/S0735- 1933(02)00309-3.

- A.N. Dravid, K.A. Smith, E.W. Merrill, P.L.T. Brian, Effect of secondary fluid motion on laminar flow heat transfer in helically coiled tubes, J. Heat Transfer 17 (1971) 1114–1122, https://doi.org/10.1002/aic.690170517.

- A. Alimoradi, F. Veysi, Prediction of heat transfer coefficients of shell and coiled tube heat exchangers using numerical method and experimental validation, Int. J.

- L. Qiu, N. Zhu, Y. Feng, E.E. Michaelides, G. Zyła, D. Jing, X. Zhang, P.M. Norris, C.

N. Markides, O. Mahian, A review of recent advances in thermophysical properties at the nanoscale: from solid state to colloids, Phys. Rep. 843 (2020) 1–81, https:// doi.org/10.1016/j.physrep.2019.12.001.

- O. Mahian, L. Kolsi, M. Amani, P. Estell´e, G. Ahmadi, C. Kleinstreuer, J.S. Marshall,

M. Siavashi, R.A. Taylor, H. Niazmand, S. Wongwises, T. Hayat, A. Kolanjiyil,

A. Kasaeian, I. Pop, Recent advances in modeling and simulation of nanofluid flows-Part I: fundamentals and theory, Phys. Rep. 790 (2019) 1–48, https://doi. org/10.1016/j.physrep.2018.11.004.

- P.C.M. Kumar, J. Kumar, S. Suresh, Experimental investigation on convective heat transfer and friction factor in a helically coiled tube with Al2O3/water nanofluid, J. Mech. Sci. Technol. 27 (2013) 239–245, https://doi.org/10.1007/s12206-012- 1206-9.

- T. Srinivas, A. Venu Vinod, Heat Transfer Enhancement using CuO/Water Nanofluid in a Shell and Helical Coil Heat Exchanger, Procedia Eng. 127 (2015) 1271–1277. doi:10.1016/j.proeng.2015.11.483.

- S. Khorasani, S. Jafarmadar, S. Pourhedayat, M.A.A. Abdollahi, A. Heydarpour, Experimental investigations on the effect of geometrical properties of helical wire turbulators on thermal performance of a helically coiled tube, Appl. Therm. Eng. 147 (2019) 983–990, https://doi.org/10.1016/j.applthermaleng.2018.09.092.

- H. Mirgolbabaei, Numerical investigation of vertical helically coiled tube heat exchangers thermal performance, Appl. Therm. Eng. (2018) 252–259, https://doi. org/10.1016/j.applthermaleng.2018.02.061.

- N. Kannadasan, K. Ramanathan, S. Suresh, Comparison of heat transfer and pressure drop in horizontal and vertical helically coiled heat exchanger with CuO/ water based nano fluids, Exp. Therm Fluid Sci. 42 (2012) 64–70, https://doi.org/ 10.1016/j.expthermflusci.2012.03.031.

- T. Srinivas, A. Venu Vinod, Heat transfer intensification in a shell and helical coil heat exchanger using water-based nanofluids, Chem. Eng. Process. Process Intensif. 102 (2016) 1–8. doi:10.1016/j.cep.2016.01.005.

- K.M. Elshazly, R.Y. Sakr, R.K. Ali, M.R. Salem, Effect of γ-Al2O3/water nanofluid on the thermal performance of shell and coil heat exchanger with different coil torsions, Heat Mass Transf. 53 (2017) 1893–1903, https://doi.org/10.1007/ s00231-016-1949-4.

- P.J. Fule, B.A. Bhanvase, S.H. Sonawane, Experimental investigation of heat transfer enhancement in helical coil heat exchangers using water based CuO nanofluid, Adv. Powder Technol. 28 (2017) 2288–2294, https://doi.org/10.1016/ j.apt.2017.06.010.

- Y.M. Ferng, W.C. Lin, C.C. Chieng, Numerically investigated effects of different Dean number and pitch size on flow and heat transfer characteristics in a helically coil-tube heat exchanger, Appl. Therm. Eng. 36 (2012) 378–385, https://doi.org/ 10.1016/j.applthermaleng.2011.10.052.

- B.A. Bhanvase, S.D. Sayankar, A. Kapre, P.J. Fule, S.H. Sonawane, Experimental investigation on intensified convective heat transfer coefficient of water based PANI nanofluid in vertical helical coiled heat exchanger, Appl. Therm. Eng. 128 (2018) 134–140, https://doi.org/10.1016/j.applthermaleng.2017.09.009.

- N. Jamshidi, M. Farhadi, K. Sedighi, D.D. Ganji, Optimization of design parameters for nanofluids flowing inside helical coils, Int. Commun. Heat Mass Transf. 39 (2012) 311–317, https://doi.org/10.1016/j.icheatmasstransfer.2011.11.013.

- G. Wang, D. Wang, J. Deng, Y. Lyu, Y. Pei, S. Xiang, Experimental and numerical study on heat transfer and flow characteristics in the shell side of helically coiled trilobal tube heat exchanger, Appl. Therm. Eng. 149 (2019) 772–787, https://doi. org/10.1016/j.ijheatmasstransfer.2019.03.137.

- S. Bahrehmand, A. Abbassi, Heat transfer and performance analysis of nanofluid flow in helically coiled tube heat exchangers, Chem. Eng. Res. Des. 109 (2016) 628–637, https://doi.org/10.1016/j.cherd.2016.03.022.

- F. Akbaridoust, M. Rakhsha, A. Abbassi, M. Saffar-Avval, Experimental and numerical investigation of nanofluid heat transfer in helically coiled tubes at constant wall temperature using dispersion model, Int. J. Heat Mass Transf. 58 (2013) 480–491, https://doi.org/10.1016/j.apt.2015.08.006.

- M. Rakhsha, F. Akbaridoust, A. Abbassi, S. Majid, Experimental and numerical investigations of turbulent forced convection flow of nano-fluid in helical coiled tubes at constant surface temperature, Powder Technol. 283 (2015) 178–189, https://doi.org/10.1016/j.powtec.2015.05.019.

- M. Mahmoudi, M.R. Tavakoli, M.A. Mirsoleimani, A. Gholami, M.R. Salimpour, Experimental and numerical investigation on forced convection heat transfer and pressure drop in helically coiled pipes using TiO2/water nanofluid, Int. J. Refrig 74 (2017) 627–643, https://doi.org/10.1016/j.ijrefrig.2016.11.014.

- M. Chandrasekar, S. Suresh, R. Srinivasan, A.C. Bose, New analytical models to investigate thermal conductivity of nanofluids, J. Nanosci. Nanotechnol. 9 (2009) 533–538, https://doi.org/10.1166/jnn.2009.J025.

- M. Attalla, H.M. Maghrabie, An experimental study on heat transfer and fluid flow of rough plate heat exchanger using Al2O3/water nanofluid, Exp. Heat Transf. 33 (2020) 261–281, https://doi.org/10.1080/08916152.2019.1625469.

- R.S. Vajjha, D.K. Das, D.P. Kulkarni, Development of new correlations for convective heat transfer and friction factor in turbulent regime for nanofluids, Int. J. Heat Mass Transf. 53 (2010) 4607–4618, https://doi.org/10.1016/j. ijheatmasstransfer.2010.06.032.

- P. Keblinski, R. Phillpot, S. Choi, A. Eastman, Mechanisms of heat flow in suspensions of nano-sized particles (nanofluids), Int. J. Heat Mass Transf. 45 (2002) 855–863.

- F. Akbaridoust, M. Rakhsha, A. Abbassi, M.S.-A. Mechanical, Experimental and numerical investigation of nanofluid heat transfer in helically coiled tubes at constant wall heat flux, Int. J. Heat Mass Transf. 26 (2015) 1483–1494, https:// doi.org/10.1016/j.apt.2015.08.006.

- M. Corcione, Empirical correlating equations for predicting the effective thermal conductivity and dynamic viscosity of nanofluids, Energy Convers. Manag. 52 (2011) 789–793, https://doi.org/10.1016/j.enconman.2010.06.072.

- Y.A. Cengel, Heat Transfer Apractical Approach, 2 nd ed, McGraw-Hill, New York, 2003.

- M.R. Salem, K.M. Elshazly, R.Y. Sakr, R.K. Ali, Experimental investigation of coil curvature effect on heat transfer and pressure drop characteristics of shell and coil heat exchanger, J. Therm. Sci. Eng. Appl. 7 (2014), 011005, https://doi.org/ 10.1115/1.4028612.

- M. Attalla, H.M. Maghrabie, E. Specht, An experimental investigation on fluid flow and heat transfer of rough mini-channel with rectangular cross section, Exp. Therm Fluid Sci. 75 (2016) 199–210, https://doi.org/10.1016/j. expthermflusci.2016.01.019.

- K. Abdul Hamid, W.H. Azmi, R. Mamat, K.V. Sharma, Heat transfer performance of TiO2–SiO2 nanofluids in a tube with wire coil inserts, Appl. Therm. Eng. 152 (2019) 275–286, https://doi.org/10.1016/j.applthermaleng.2019.02.083.

- J.P. Holman, Experimental Methods for Engineers, 8th ed, McGraw-Hill, 2012.

- M. Attalla, Experimental investigation of heat transfer and pressure drop of SiO2/ water nanofluid through conduits with altered cross-sectional shapes, Heat Mass Transf. Und Stoffuebertragung. 55 (2019) 3427–3442, https://doi.org/10.1007/ s00231-019-02668-0.

- G. Huminic, A. Huminic, Heat transfer and entropy generation analyses of nanofluids in helically coiled tube-in-tube heat exchangers, Int. Commun. Heat Mass Transf. 71 (2016) 118–125, https://doi.org/10.1016/j. icheatmasstransfer.2015.12.031.

- P. Naphon, S. Wongwises, A review of flow and heat transfer characteristics in curved tubes, Renew. Sustain. Energy Rev. 10 (2006) 463–490, https://doi.org/ 10.1016/j.rser.2004.09.014.

- K. Narrein, H.A. Mohammed, Influence of nanofluids and rotation on helically coiled tube heat exchanger performance, Thermochim Acta 564 (2013) 13–23, https://doi.org/10.1016/j.tca.2013.04.004.

- L. Guo, Z. Feng, X. Chen, An experimental investigation of the frictional pressure drop of steam-water two-phase flow in helical coils, Int. J. Heat Mass Transf. 44 (2001) 2601–2610, https://doi.org/10.1016/S0017-9310(00)00312-4.

- N. Jamshidi, M. Farhadi, D.D. Ganji, K. Sedighi, Experimental analysis of heat transfer enhancement in shell and helical tube heat exchangers, Appl. Therm. Eng. 51 (2013) 644–652, https://doi.org/10.1016/j.applthermaleng.2012.10.008.